## Dropdown Menus - HIDE SHEET (hidden)
Asset Category | Asset Product List | Current Condition | Yes/No Questions | Current Status | Capacity | Importance
Pump | Pump Product | Excellent | Yes | Active | At capacity | None
Hydrant | Hydrant Product | Good | No | Back-up | Below capacity | Less than 25%
Meter | Meter Product | Fair | Unknown |  | Beyond capacity | 25-50%
Pipe | Pipe Product | Poor |  |  |  | 50-75%
Source | Source Product | Very Poor |  |  |  | Greater than 75%
Storage | Storage Product
Analytical Equipment | Analytical Equipment Product
Treatment | Control System Product
Valve | Treatment Product
Control System | Valve Product
Safety Equipment | Other Product
Other

## Asset Tables - HIDE SHEET (hidden)
Pump | Hydrant | Meter | Pipe | Source | Storage | Other | Treatment | Valve | Control System | Analytical Equipment | Safety Equipment
Submersible Well Pump | Fire | Master | Polyvinyl Chloride (PVC) | Well | Bolted, Welded, or Glass Fused Steel Tank | Building | Sedimentation | Gate | Telemetry | pH Meter | Add details in Asset Description
Vertical Turbine Pump | Flush | Well | Ductile Iron (DI) | Intake Structure | Concrete Tank | Vehicle | Filtration | Ball | SCADA | Chlorine Monitor
High Service Pump | Flow Test | Source | Steel | Consecutive Connection | Plastic or Polymer Tank | Computer | Chlorination | Butterfly | Variable Frequency Drive | Other Remote Sensor
Booster | Other | Residential | Cast Iron | Springs | Fiberglass Tank/Structure | Electrical | Ozonation | Pressure Relief (PRV) | Motor Control Center
Transfer |  | Commercial | Concrete | Reservoir | Earthen Basin or Reservoir | Lab Equipment | Ultraviolet Disinfection | Air Release (ARV) | Other Programmable Logic Control (PLC)
Metering |  | Other | Asbestos Cement (AC) | Other | Hydropneumatic/Captive Air Tank | Generator | Ion Exchange or Other Media-type Treatment | Air Vacuum | Other Power Supply
Chemical Feed Pump |  |  | Service Line |  | Other | Tools | Solids Handling | Check | Other Communication System
Surface Water Intake |  |  | Lead Service Line |  |  | Other | Fluoride | Altitude
Backwash |  |  | Other |  |  |  | Corrosion Control
Motor | [6 empty] | Other
Other

## Est. Useful Life - HIDE SHEET (hidden)
For Lookup | Asset Category | Asset Type | Estimated Useful Life
HydrantFire | Hydrant | Fire | 50
HydrantFlush | Hydrant | Flush | 50
HydrantFlow Test | Hydrant | Flow Test | 50
HydrantOther | Hydrant | Other | 50
MeterMaster | Meter | Master | 15
MeterWell | Meter | Well | 15
MeterSource | Meter | Source | 15
MeterResidential | Meter | Residential | 15
MeterCommercial | Meter | Commercial | 15
MeterOther | Meter | Other | 15
OtherBuilding | Other | Building | 50
OtherVehicle | Other | Vehicle | 10
OtherComputer | Other | Computer | 5
OtherElectrical | Other | Electrical | 20
OtherGenerator | Other | Generator | 10
OtherLab Equipment | Other | Lab Equipment | 5
OtherTools | Other | Tools | 15
OtherOther | Other | Other | 10
PipePolyvinyl Chloride (PVC) | Pipe | Polyvinyl Chloride (PVC) | 80
PipeDuctile Iron (DI) | Pipe | Ductile Iron (DI) | 80
PipeSteel | Pipe | Steel | 50
PipeCast Iron | Pipe | Cast Iron | 80
PipeConcrete | Pipe | Concrete | 80
PipeAsbestos Cement (AC) | Pipe | Asbestos Cement (AC) | 80
PipeService Line | Pipe | Service Line | 50
PipeLead Service Line | Pipe | Lead Service Line | 20
PipeOther | Pipe | Other | 50
PumpSubmersible Well Pump | Pump | Submersible Well Pump | 15
PumpVertical Turbine Pump | Pump | Vertical Turbine Pump | 15
PumpHigh Service Pump | Pump | High Service Pump | 15
PumpBooster | Pump | Booster | 15
PumpTransfer | Pump | Transfer | 15
PumpMetering | Pump | Metering | 10
PumpChemical Feed Pump | Pump | Chemical Feed Pump | 5
PumpSurface Water Intake | Pump | Surface Water Intake | 15
PumpOther | Pump | Other | 15
PumpBackwash | Pump | Backwash | 15
PumpMotor | Pump | Motor | 15
SourceWell | Source | Well | 50
SourceIntake Structure | Source | Intake Structure | 40
SourceConsecutive Connection | Source | Consecutive Connection | 20
SourceReservoir | Source | Reservoir | 80
SourceOther | Source | Other | Undefined
SourceSprings | Source | Springs | 20
StorageBolted, Welded, or Glass Fused Steel Tank | Storage | Bolted, Welded, or Glass Fused Steel Tank | 50
StorageConcrete Tank | Storage | Concrete Tank | 50
StoragePlastic or Polymer Tank | Storage | Plastic or Polymer Tank | 50
StorageFiberglass Tank/Structure | Storage | Fiberglass Tank/Structure | 50
StorageEarthen Basin or Reservoir | Storage | Earthen Basin or Reservoir | 50
StorageHydropneumatic/Captive Air Tank | Storage | Hydropneumatic/Captive Air Tank | 15
StorageOther | Storage | Other | 50
TreatmentChlorination | Treatment | Chlorination | 10
TreatmentFiltration | Treatment | Filtration | 30
TreatmentOzonation | Treatment | Ozonation | 10
TreatmentUltraviolet Disinfection | Treatment | Ultraviolet Disinfection | 10
TreatmentSolids Handling | Treatment | Solids Handling | 10
TreatmentIon Exchange or Other Media-type Treatment | Treatment | Ion Exchange or Other Media-type Treatment | 25
TreatmentSedimentation | Treatment | Sedimentation | 25
TreatmentFluoride | Treatment | Fluoride | 10
TreatmentCorrosion Control | Treatment | Corrosion Control | 10
TreatmentOther | Treatment | Other | 10
UnknownUnknown | Unknown | Unknown | Undefined
ValveGate | Valve | Gate | 20
ValveBall | Valve | Ball | 20
ValveButterfly | Valve | Butterfly | 20
ValvePressure Relief (PRV) | Valve | Pressure Relief (PRV) | 20
ValveAir Release (ARV) | Valve | Air Release (ARV) | 20
ValveAir Vacuum | Valve | Air Vacuum | 20
ValveCheck | Valve | Check | 15
ValveAltitude | Valve | Altitude | 20
Analytical EquipmentpH Meter | Analytical Equipment | pH Meter | 15
Analytical EquipmentChlorine Monitor | Analytical Equipment | Chlorine Monitor | 15
Analytical EquipmentOther Remote Sensor | Analytical Equipment | Other Remote Sensor | 15
Control SystemTelemetry | Control System | Telemetry | 10
Control SystemSCADA | Control System | SCADA | 10
Control SystemVariable Frequency Drive | Control System | Variable Frequency Drive | 10
Control SystemMotor Control Center | Control System | Motor Control Center | 10
Control SystemOther Power Supply | Control System | Other Power Supply | 25
Control SystemOther Communication System | Control System | Other Communication System | 10
Control SystemOther Programmable Logic Control (PLC) | Control System | Other Programmable Logic Control (PLC) | 10
Safety EquipmentAdd details in Asset Description | Safety Equipment | Add details in Asset Description | Undefined

## Weighting Tables - HIDE SHEET (hidden)
Question | Tab(s) | Weight | Calculation | Total Maximum Score
Current Condition | Condition Assessment; Vulnerabiliity Assessment | 1 | Condition Assessment | 5
Reliability | Condition Assessment; Vulnerability Assessment | 1 | Consequence of Failure | 7
Current Status | Condition Assessment | 1 | Probability of Failure | 5
Importance | Vulnerability Assessment | 1
Compliance | Vulnerability Assessment | 1
Estimated Remaining Life | Vulnerability Assessment | 1
Capacity | Vulnerability Assessment | 1
Repair Schedule | Vulnerability Assessment | 1
Redundancy | Critical Assets | 1
Public Health and Environment | Vulnerability Assessment | 2

## 0a_Basic Information
Small Community Assistance Planning (SCAP) Tool
Drinking Water Assets
U.S. Environmental Protection Agency Region 7
Move left to right to ensure the accurate dropdown menus are available for selection. Cells colored Blue contain dropdown menus for selection. Cells colored Red are for manually entering information. Cells colored Yellow are auto-filled, but can be overwritten. Cells colored Gray are for manually entering optional information. Cells colored Green are calculated output values.
FILL IN THE INFORMATION BELOW
Utility Name:
Utility Location:
Date of Inventory:
System Capacity:
Population Served:
Number of Connections:
Assessor Name:
This inventory is for DRINKING WATER assets only. Utilities with wastewater assets should complete a separate inventory using the Wastewater tool.

## 1_Asset Inventory
| INSTRUCTIONS: Enter information in cells, either manually or using dropdown menus. Move left to right to ensure the accurate dropdown menus are available for selection. Cells colored Blue contain dropdown menus for selection. Cells colored Red are for manually entering mandatory information. Cells colored Yellow are auto-filled, but can be overwritten. Cells colored Gray are for manually entering optional information. |  |  |  |  | Additional resources:
Asset Management: A Guide for Water and Wastewater Systems
Asset Management: A Handbook for Small Water Systems
Asset Management for Small Utilities
Sustainable Infrastructure Management Program Learning Environment
Taking Stock of your Small Water System: A Simple Asset Inventory for Very Small Water Systems
| Key Information | [10 empty] | Supplemental Information
ID | Asset Category (select first) | Asset Type | Asset Description | System Area | Asset ID | Estimated Useful Life (in years) | Estimated Installation Date (M/D/YYYY) | Remaining Useful Life (in years) | Location | Comments for Inspection, Rehab, or Repair | Operational | Alternate Asset ID | Size/Capacity | Number/ Length/ Notes | Product Information | Estimated Replacement Cost | Model Name/Number | Serial Number | Column1 | Column2 | Column3
[21 empty] | 0 | 0 | 0
Formulas:
Remaining Useful Life (in years) = IF(ISNUMBER([Estimated Useful Life (in years)]),IF(ISNUMBER([Estimated Installation Date (M/D/YYYY)]),IF(([Estimated Useful Life (in years)]-(INT((TODAY()-[Estimated Installation Date (M/D/YYYY)])/365)))<0,0,[Estimated Useful Life (in years)]-(INT((TODAY()-[Estimated Installation Date (M/D/YYYY)])/365))),""),"")

## 2a_Condition Assessment
| INSTRUCTIONS: Enter information in cells, either manually or using dropdown menus. Cells colored Blue contain dropdown menus for selection. Cells colored Yellow are values from previous sheets and cannot be edited. Cells colored Green are calculated output values. |  |  |  | Additional resources:
Asset Management for Your Water System
Asset Management Manual: A.M. Kan Work! - Section 3 and Appendix A
Condition Assessment Strategies and Protocols for Water and Wastewater Utility Assets - Appendix C
Fundamentals of Asset Management - Slide 15
ID | Asset Category and Type | Asset Description | Remaining Useful Life | Current Condition of Asset | Reliability - Does the asset need frequent repairs in addition to routine maintenance? | Condition Assessment Score (higher score indicates elevated concern)

## 2c_Critical Assets
| INSTRUCTIONS: No selections are required for this sheet. Users should review information here to ensure it is correct. Cells colored Yellow are values from previous sheets and cannot be edited. Cells colored Green are calculated output values. The final outputs of this tool are the Criticality Score, Combined Score, and Rank Columns. | [5 empty] | Additional resources:
Asset Management for Your Water System
Developing Asset Management Plans Using CUPSS
Asset Management: A Guide for Water and Wastewater Systems
Asset Management Manual: A.M. Kan Work! - Section 3 and Appendix A
ID | Asset Category and Type | Asset Description | CoF Score | PoF Score | Redundancy | Condition Assessment Score | Criticality Score (higher number indicates more critical) | Combined Score (higher number indicates more critical) | Rank (ordered from highest priority asset [highest score] to lower priority assets)

## 3a_Product Lists - USER SHEET
Pump Product | Contact Info | Hydrant Product | Contact Info | Meter Product | Contact Info | Pipe Product | Contact Info | Source Product | Contact Info | Storage Product | Contact Info
Other Product | Contact Info | Treatment Product | Contact Info | Valve Product | Contact Info | Control System Product | Contact Info | Analytical Equipment Product | Contact Info

## 3b_Additional Resources
Resource | Organization | Description
Asset Management: A Guide for Water and Wastewater Systems | Southwest Environmental Finance Center (formerly the New Mexico Environmental Finance Center) | Guidebook outlining the purpose and core steps of asset management.
Asset Management: A Handbook for Small Water Systems | U.S. Environmental Protection Agency | Step-wise introduction to the principles of asset management, for small community water systems
Asset Management Manual: A.M. Kan Work! | Southwest Environmental Finance Center | Comprehensive asset management and energy efficiency manual for water and wastewater systems, including video clips from water system and community representatives
Asset Management for Small Utilities | Water Environment Research Foundation | Guidelines and worksheets for asset inventories, priority ranking, and asset management plan implementation
Asset Management for Your Water System | West Virginia Department of Health and Human Resources | Guidance documents, worksheet tools, and supplemental resources for developing an asset management plan
Condition Assessment Strategies and Protocols for Water and Wastewater Utility Assets - Appendix C | Water Environment Research Foundation | Guidance on conducting condition assessments for water and wastewater assets
Fundamentals of Asset Management | U.S. Environmental Protection Agency | Ten-module, slide-based training on developing an asset management program
Sustainable Infrastructure Management Program Learning Environment | Water Environment Research Foundation | On-line learning environment and supplemental resources for developing asset management plans
Taking Stock of your Small Water System: A Simple Asset Inventory for Very Small Water Systems | U.S. Environmental Protection Agency | Guide for small water systems on developing a simple asset inventory

## 3b_Condition Rating Guidance
Asset Category | Condition Ratings Guidance | Notes
Pump | Motor Hours: Excellent = <1,000 hrs; Good = 10,000-50,00 hrs; Fair = 50,000-100,000 hrs; Poor = 100,000-200,000 hrs; Very Poor = >200,000 hrs Vibrations Detected: Excellent = No unusual vibrations; Good = Minor; Fair = Moderate; Poor = Considerable; Very Poor = Major Temperature: Excellent = No unusual temp; Good = Minimal heat; Fair = Heat detected by hand; Poor = Heat uncomfortable to touch; Very Poor = Too hot to touch Noise: Excellent = No unusual noise; Good = Slight whine/rattle; Fair = Moderate whine/rattle heard over pump noise; Poor = Loud whine/rattle; Very Poor = Disturbingly loud Leaking Seals: Excellent = No visible signs; Good = Minor leaking seals; Fair = Moderate leaking seals; Poor = Considerate leaking seals; Very Poor = Major leaking seals | Assessment of temperature and leaking seals will not be possible for submersible pumps.
Hydrant | Operation: Excellent = Fully operational; Good = Slight resistance when opening/closing; Fair = Moderate resistance in stem when opening/closing; Poor = Considerable resistance in stem when opening/closing; Very Poor = Unable to open/close Missing/defective Items: Excellent = None; Good = Rounded operating nut; Fair = Missing cap and/or rounded operating nut; Poor = Defective items, missing items, rounded nuts; Very Poor = Missing parts, misaligned nozzles, rounded operating nuts, considerable deficiency Paint Condition: Excellent = Great condition; Good = Good condition; Fair = Moderate condition, chips in paint; Poor = Paint chipped, dulled, thin in areas; Very Poor = Poor condition, chipped or faded paint
Meter | Accuracy: Excellent = No slowdown detected; Good = Slight decrease in average demand; Fair = Noticeable decrease in average demand; Poor = Considerable decrease in average demand; Very Poor = Meter register does not move between montly readings Leaks: Excellent = No visible water in meter pit or in meter; Good = Slight condensation on glass; Fair = Moderate water in meter pit and/or water behind glass; Poor = Considerable water in meter pit and/or water behind glass; Very Poor = Major water in meter pit and/or water behind glass, visibly leaking from meter setter. Years Since Last Calibration (Flow Meters): Excellent = <1 year; Good = 1-2 years; Fair = 2-3 years; Poor = 3-4 years; Very Poor = >4 years Unplanned Outages: Excellent = 0/year; Good = 1/year; Fair = 2/year; Poor = 3/year; Very Poor = More than 3/year
Pipe | Number of Leaks or Breaks in Past 5 Years: Excellent = 0 leaks or breaks per mile; Good = 1 leak or break per mile per year; Fair = 2 leaks or breaks per mile per year; Poor = 3-4 leaks or breaks per mile per year; Very Poor = >4 leaks or breaks per mile per year CCTV Inspection: Excellent = Clean pipe walls, no illegal connections, no visible leaks. Good = Minor tuburculation or buildup on pipe walls, no illegal connections, no visible leaks; Fair = Minor tuburculation or build up on pipe walls, no illegal connections, some minor leaks; Poor = Moderate tuburculation or build up on pipe walls, no illegal connections, minor to substantial leaks visible. Very Poor = Any of the following - excessive tuburculation or build up on pipe walls substantially restricting flow, one or more illegal connection, substantial leaks, one or more breaks in pipe.
Source | Surface Water Intake Screen: Excellent = Screen and piping in good shape; Good = Minor visible deterioration of screen and/or pipe; Fair = Moderate visible deterioration of screen and/or pipe; Poor = Considerable deterioration of screen and/or pipe; Very Poor = Screen and/or pipe are severaly damaged/deteriorated/missing Well: Excellent = No apparent signs of deterioration of casing or well head, no reduction in static water level or well production; Good = Minor deterioration of casing, well head, or capacity; Fair = Moderate deterioration of casing, well head, or production; Fair = Considerable deterioration of casing, well head or production; Very Poor = Well is no longer producing adequate supply and/or has experienced substantial deterioration of well casing or well head. Raw Water Dike/Reservoir Walls: Excellent = Stable slope, no unwanted vegetation; Good = Some erosion of walls, some unwanted vegetation; Fair = Moderate deterioration of walls and/or unwanted vegetation; Poor = Considerable deterioration of walls and/or unwanted vegetation; Very Poor = Substantial deterioration of walls and/or excessive unwanted vegetation. Raw Water Reservoir Sedimentation: Excellent = No build up of sedimentation. Good = Minor sedimentation at bottom of reservoir; Fair = Moderate sedimentation but not yet affecting storage capacity; Poor = Considerable sedimentation affecting storage capacity; Very Poor = Substantial sedimentation having impact on storage capacity and carry over to intake/discharge.
Storage | Storage Capacity: Excellent = At least 20% growth available; Good = At least 15% growth available; Fair = At least 10% growth available; Poor = At least 5% growth available; Very Poor = 0% growth available Exterior Paint/Tank Exterior: Excellent = No chipping or visible thin spots; Good = Minor areas of chipping, rust or thin areas; Fair = Moderate chipping, rust, cracks or thin areas; Poor = Considerable chipping, rust, cracks, or thin areas; Very Poor = Major cracks, thin areas, or visible leaks Hydropneumatic/Captive Air Tank: Excellent = No visible deterioration, proper pump run times; Good = Minor visible deterioration, occasional pump run issues; Fair = Moderate deterioration of tank and/or piping and occasional pump run issues; Poor = Considerable visible deterioration of tank and/or piping, no longer achieving recommend pump run times; Very Poor = Major visible deterioration of tank, leaking of tank and/or piping, excessive pump run times an on-going problem. Fencing and Gate: Excellent = The site is secure; Good = Security devices have minor damage but no unauthorized personnel can enter; Fair = Moderate damage allowing unauthorized persons to enter; Poor = Considerable damage to security devices; Very Poor = No security/site exposed to threat Earthen Basin Dike/Reservoir Walls: Excellent = Stable slope, no unwanted vegetation; Good = Some erosion of walls, some unwanted vegetation; Fair = Moderate deterioration of walls and/or unwanted vegetation; Poor = Considerable deterioration of walls and/or unwanted vegetation; Very Poor = Substantial deterioration of walls and/or excessive unwanted vegetation. Earthen Basin Sedimentation: Excellent = No build up of sedimentation. Good = Minor sedimentation at bottom of reservoir; Fair = Moderate sedimentation but not yet affecting storage capacity; Poor = Considerable sedimentation affecting storage capacity; Very Poor = Substantial sedimentation having impact on storage capacity and carry over to intake/discharge. Other things to consider: Leaking of tank, concrete ringwall condition, condition of vents/hatch/overflow
Other | Building: Excellent = No deterioratoin of siding, roof, foundation, doors and windows; Good = Some deterioration; Fair = Moderate deterioration; Poor = Considerable deterioration; Very Poor = Substantial deterioration Generator: Excellent = No visible deterioration, fully operable whenever needed. Good = Minor deterioration and/or some difficulty in start up; Fair = Moderate deterioration and/or difficult to start when needed; Poor = Considerable deterioration and/or does not start or remain running as needed; Very Poor = Substantial deterioration and not reliable to start or run as needed. Vehicles: Excellent = No deterioration and runs reliably; Good = Some deterioration but runs reliably. Fair = Moderate deterioration and some engine repair needed; Poor = Considerable deterioration and engine repair needed; Very Poor = Substantial deterioration, engine repair needed, does not run reliably. Other things to consider: Assets operating within manufacturers' recommendations.
Treatment | Condition of Ion Exhange Media Treatment Vessel: Excellent = No visible deterioration of vessel, media very recently replaced; Good = Minor visible deterioration of vessel, media recently replaced/regenerated; Fair = Moderate visible deterioration of vessel, media still within expected life; Poor = Considerable visible deterioration, media in need of regeneration or replacement; Very Poor = Substantial deterioration of media vessel including possible leaking, media in need of replacement. Condition of Filter Media: Excellent = No visible deposits or change in media color, no loss of media depth; Good = Minor visible deposits or change in media color, some loss of media depth; Fair = Moderate deposits and visible change in color and/or loss of media depth; Poor = Considerable visible deposits or change in media color and/or considerable loss of media depth; Very Poor = Heavy deposits and visible color change and/or substantial loss of media depth. Plant Flow Output: Excellent = Flow within 5% of expected output; Good = Flow within 10% of expected output; Fair = Flow within 15% of expected output; Poor = Flow within 40% of expected output; Very Poor = Flow < 40% of expected output Filtered Water Turbidity: Excellent = Continually meets required level; Good = Rarely exceeds required level; Fair = Occasionally exceeds required level; Poor = Occasionally exceeds required level and is out of compliance; Very Poor = Frequently exceeds required level and is out of compliance Chemical Feed Lines: Excellent = No detectable leakage; Good = Minor detectable leakage; Fair = Moderate detectable leakage; Poor = Considerable detectable leakage; Very Poor = Heavy detectable leakage Unplanned Outages: Excellent = 0/year; Good = 1/year; Fair = 2/year; Poor = 3/year; Very Poor = >3 per year
Valve | Operation: Excellent = Easy to operate; Good = Minor resistance to operation; Fair = Moderate resistance to operation; Poor = Very hard to operates; Very Poor = cannot operate valve Valve Box and Cover: Excellent = Good condition; Good = Minor deficiencies; Fair = Moderate deficiencies; Poor = Considerable deficiencies; Very Poor = Cracks in valve box or missing/damaged cover Leakage: Excellent = No detectable leakage; Good = Minor detectable leakage; Fair = Moderate leakage but servicable; Poor = Considerable leakage, barely servicable; Very Poor = Heavy leakage, not servicable Paking Leakage: Excellent = The site is secure; Good = Security devices have minor damage but no unauthorized personnel can enter; Fair = Moderate damage allowing unauthorized persons to enter; Poor = Considerable damage to security devices; Very Poor = No security/site exposed to threat | Leakage of valve and packing difficult to assess for buried distribution valves.
Control System | Controls: Excellent = Fully operational, just updated. Good = Minor issues with operability, recently updated; Fair = Moderate issues with operability, updates due; Poor = Considerable issues with operability, updates required and overdue; Very Poor = Substantial issues with operability, updates requried and long overdue. Other things to consider: Controls operating within manufacturers' recommendations.